## Solar Contribution
DLI FACILITY DOMESTIC HOT WATER DESIGN TEMPLATE |  |  |  | 2024-09-27
|  | inputs | Location | Alice Springs
Item | THERMAL ENERGY |  |  | Notes
1.0 | HW GENERATION |  |  |  | 1 | Climate Maps - Temperature Latest (bom.gov.au)
1.1 | Average HW Demand from Building Loading | 1500 | L/day |  | 2 | ASHRAE Handbook HVAC Applications 2019, Chapter 51: Serviced Water Heating
1.2 | Ambient Water Temperature 1 | 26 | °C | Refer BOM Climate map, water temp 2°C less than ambient air temp | 3 | Ignoring minor losses associated with heating device cycling, and cooling of dead legs
1.3 | Generation Temperature | 65 | °C | AS/NZS 3500.4 Section 10, 10.2
1.4 | Daily Generation Energy | 68.0225 | kWh
2.0 | RECIRCULATION THERMAL LOSS
2.1 | Total HW Fixtures in Building | 25 | no | Estimated if unknown
2.2 | Recirculation Flow Allowance per fixture 2 | 0.003 | L/s/fixture | Approximation, since Building reticulation likely unknown
2.3 | Recirculated Flow | 6480 | L/day
2.4 | Generation Temperature | 65 | °C | AS/NZS 3500.4 Section 10, 10.2 requires minimum 60°C
2.5 | Return Temperature | 60 | °C | AS/NZS 3500.4 Section 10, 10.2 requires minimum 55°C
2.6 | Daily Reheat Energy | 37.674 | kWh
3.0 | TOTAL DAILY THERMAL ENERGY 3 | 105.6965 | kWh/day
4.0 | SOLAR CONTRIBUTION
4.1 | Average Hot Water Demand from Building Loading | 1500 | L/day | From Item 1.0 above | Tank Selector
4.2 | Selected Tank Volume (410L or 1,000L) | 410 | L | Use drop down selector in C19 | 410 | L
4.3 | Proposed no. of tanks, based on available area | 4 | no |  | 1000 | L
4.4 | Actual Stored Volume | 1640 | L | Volume should meet daily demand if plant area available
4.5 | Selected Ratio Tank Volume to Collector Area | 55 | L/m2 | AS/NZS 3500.4 requires 40L/m2 < 90L/m2
4.6 | Surface Area of Solar Collectors required | 29.8182 | m2
4.7 | Equivalent even number of Solar Collectors | 18 |  | At 1.86m2/collector
4.8 | Average Daily Solar Radiation at Site (ex AS/NZS 3500.4) | 21.4 | MJ/m2/day | Refer AS/NZS 3500.4, Figure G.3(B)
4.9 | Average Daily Solar Radiation converted to kWh | 5.9445 | kWh/m2/day
4.10 | Annual Average Collector Efficiency | 60% |  | Industry standard
4.11 | Average Daily Energy from Collectors | 119.413 | kWh/day
4.12 | Daily Storage Heat Loss from Tanks | -11.72 | kWh/day | Based on AS/NZS 4692.2:2005
4.13 | Average Solar Energy Available | 107.693 | kWh/day
4.14 | Daily HW Generation Energy Required | 105.6965 | kWh/day | From Item 3.0 above
4.15 | Theoretical Solar Contribution (TSC) | 101.9% |  | Adjust tanks & ratio to collectors so TSC ~ 100%
4.16 | Anticipated Solar Fraction at Location | 94% |  | Refer Table G1 - AS/NZS3500.4
4.17 | Average Solar Energy Available from Collectors at Location | 99.3547 | kWh/day
4.18 | AVERAGE SOLAR CONTRIBUTION | 94%
2.958