## Heat_Pumps
NORTHERN TERRITORY DEPARTMENT OF LOGISTICS AND INFRASTRUCTURE (DLI) COMMERCIAL HEAT PUMP MARKET RESEARCH - 2026 UPDATE
Original information provided by DLI's consultants in 2023, subsequent supplier updates included as noted in Distributor column.
Models with refrigerant Global Warming Potential (GWP) > 700 crossed out as not complying with DLI Minimum Design Standard requirements (and use would be a particular future supply risk given Australian Government phase out requirements)
COP information provided by suppliers, not veriifed by DLI or checked against separate EUROVENT/AHRI certified COPs
Designers need to review WaterMark certification status for models, whether heat exchangers need to be included in designs, and the impact on system COPs
DLI is not responsible for the accuracy of information contained here. All information is as provided by consultants or suppliers and needs to be checked.
Manufacturer | Distributor | Contact details | Application | Type | Refrigerant | Capacity Range kW | Max. Hot Water Temp. | Warranty period (years) | Warranty water quality conditions | COP to deliver 60oC from 28oC water (nominal Darwin conditions) | COP to deliver 60oC from 13oC water (nominal Alice Springs conditions) | Minimum ambient water temperature can heat to 60oC from (without relying on electric element) | Energy Efficiency Certifcation | Applicable Standards for energy performance rating and certification | Applicable Standards for acoustic performance rating | Additional information
TRANE | TRANE AUSTRALIA | Patrick.Tan@Tranetechnologies.com | Large Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll | HFO R454b HFC R32 Propane R290 HFC 410a | 5 - 700 | 77° C | 1 | "Heat-pumps we supply are intended to be integrated into a closed loop system, with appropriate water treatment maintained to prevent any scale or corrosion. Under normal circumstances, we do not foresee any warranty issues. " | 2.62 - 2.99 | 2.62 - 2.99 | TBC | EUROVENT/AHRI | EN14825 EN14511 ASHRAE 90.1 AHRI 551/591 | ISO 9614
| (Updated 14/7/2026) |  | Large Commercial/Industrial Space Heating | Air-Sourced / Screw | HFC R513a HFC R134a | 350 - 2000 | 55° C | 1 |  | 2.64 - 2.96 | 2.67 - 2.96 | TBC
|  |  | Large Commercial/Residential Space Heating, DHW | Water-Sourced / Scroll | HFC R513a HFC R134a HFC R454b | 40 - 700 | 65° C | 1 |  | 2.37 - 2.43 | 2.37 - 2.43 | TBC
|  |  | Large Commercial/Industrial Space Heating, DHW | Water-Sourced / Screw | HFO R1234ze HFO R1233zd(e) HFC R515b HFC R134a | 175 - 3200 | 110° C | 1 |  | 3.08 - 3.58 | 3.08 - 3.58 | TBC
|  |  |  | Water-Sourced / Magnetic-Bearing Centrifugal | HFO R1234ze HFC R515b | 400 - 1500 | 65° C | 1 |  | 4.2 - 4.53 | 4.2 - 4.53 | TBC
CARRIER | CARRIER AUSTRALIA (Updated 27-7-2026) | Rory.Connaughton@carrier.com | Large Commercial/Residential Space Heating, DHW | Air-Sourced / Multi-Scroll | HFC R32 Propane R290 HFC R410A | 40 - 1000 | 90° C | 5 |  |  |  |  | EUROVENT/AHRI | EN14825 EN14511 ASHRAE 90.1 AHRI 551/592 | ISO 9614
|  |  | Large Commercial/Industrial Space Heating | Air-Sourced / Screw | HFC R134A | 380-1400 | 55° C | 5
|  |  | Large Commercial/Industrial Space Heating | Water-Sourced / Screw | HFO R1234ze HFC R515A HFC R515B HFC R513A HFC R32 HFC R410A | 20 - 2500 | 85° C | 5
REVERE | AUTOMATIC HEATING (Updated 22-7-2026) | cameron.crowther@automaticheating.com.au | Small Commercial/Residential DHW | Air-Sourced / Scroll & Piston | CO2 R744 | 5 - 80 | 90° C | 2 plus extended warranty available | Limits: 600 mg/L TDS 200 mg/L CaCO3 -1 to .4 LSI 5.5-9.5 pH 19 mg/L CO2 300 mg/L Chlorides | ~3.5 @ 60C ~4.1 @ 65C in 18C ambient | ~3.2-4.5 in 5C ambient | -25C | EUROVENT | EN14825 EN14511 | ISO 9614
|  |  | Small Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll & Piston | Propane R290 | 2.6-132 | 75° C |  |  | ~3.41 for 60C ~3.29 for 65C in 20C ambient | ~2.38 for 60C ~2.36 for 65C in 5C ambient | -25C
|  |  | Small Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll | HFC R32 HFC R410a | 2 - 25 | 60° C |  |  | ~2.73 for 60C in 20C ambient | ~2.25 for 60C in 5C ambient | -25C
RHEEM | RHEEM (Updated 12/10/2027) | simon.yon@rheem.com.au | Small Residential DHW | Air-Sourced / Rotary | R513a | 5 | 60° C | (180L) 7 year on Cylinder |  |  | 4.9 @ 19C | -7 | N/A | N/A | Noise levels measured in free-field conditions per the procedures outlined in AS 1217.7 | WaterMark / EMC Compliance
|  |  | Small Residential DHW | Air-Sourced / Rotary | R513a | 5 | 60° C | (270L) 10 Year on Cylinder |  | 5.1 @ 33.5C | 4.4 @ 19C | -7 |  |  |  | WaterMark / EMC Compliance
|  |  | Small Residential DHW | Air-Sourced / Rotary | R290 | 5 | 60° C | (280L) 10 Year on Cylinder |  | 5.9 @ 33C | 4.5 @ 19C | -7 |  |  |  | WaterMark / EMC Compliance
|  |  | Small Residential DHW | Air-Sourced / Rotary | R290 - SPLIT | 5 | 65° C | (325L) 10 Year on Cylinder |  | 6.6 @ 33C | 5.2 @ 19C | -7 |  |  |  | WaterMark / EMC Compliance
|  |  | Small Commercial/Residential DHW DHW | Air-Sourced / Sroll | HFC R134a | 18-40 | 65° C | 1 year - all componets 2 years - Sealed System |  | 4.59-4.68 | 4.59-4.68 | 0C |  |  |  | WaterMark / EMC Compliance
|  |  | Small Commercial/Residential DHW | Air-Sourced/ Scroll | HFO R1234yf | 15-30 | 65° C | 1 year - all componets 2 years - Sealed System |  | 4.8 | 4.28 | 0C |  |  |  | WaterMark / EMC Compliance
|  |  | Small Commercial/Residential DHW | Water - Sourced / Scroll | HFO R1234yf | 15-30 | 65° C | 1 year - all componets 2 years - Sealed System |  | 5.2-6.9 | 5.2-6.9 | 0C |  |  |  | WaterMark / EMC Compliance
RINNAI | RINNAI (Updated 07-10-2026) | Stuart Swift StuartS@rinnai.com.au | Small to large Commercial/Residential DHW | Air-Sourced / Sroll | Propane R290 | 25kW & 50kW | 70° C | 2 Year | Total Dissolved Solids (TDS) mg/Litre or ppm: 600 or 2500 - Hardness (as CaCO3 ) mg/Litre or ppm: 200 - Saturation Index (Langelier): +0.4 to -1.0 @65°C - pH: 5.5 to 9.5 - Dissolved CO2 mg/Litre or ppm: N/A - Chlorides mg/Litre or ppm:300 | CHP025: 4.4 @ 20C Ambient and 39C Entering Water, CHP050: 4.2 @ 20C Ambient and 39C Entering Water | CHP025: 4.4 @ 20C Ambient and 39C Entering Water, CHP050: 4.2 @ 20C Ambient and 39C Entering Water | -5C to +50C
STIEBEL-ELTRON | STIEBEL-ELTRON | daniel.thompson@stiebel-eltron.com.au | Small Commercial/Residential DHW | Air-Sourced / Sroll | Propane R290 | 10KW,13KW,17KW | 75° C |  |  | Average COP 3.8 | Average COP 3.0 |  | EUROVENT | EN14825 EN14511 | ISO 9614
| (Updated 13/7/2026) |  | Large Commercial/Residential DHW | Air-Sourced / Sroll
RHOSS | INDUSTRIAL AIR (Updated 9-10-2026) | Steven Cook, steven@industrialair.com.au | Small Commercial/Residential Space Heating, Cooling,DHW | Air-Sourced / Inverter Rotary | HFC R32 | 6-16.0 | 60° C | 1 year standard - up to 5 years at additional cost |  | 4.01 cop 60LWT 16.5 ambient | 1.89 cop 60LWT -1 ambient | 5 | EUROVENT | EN14825 EN14511 | ISO 9614 | Electa-ECO
|  |  | Small Commercial/Residential Space Heating, Cooling,DHW | Air-Sourced / Inverter Rotary | HFC R32 | 18-30 | 60° C | 1 year standard - up to 5 years at additional cost | #VALUE! | 3.17 cop 60LWT 16.5 Ambient | 1.7 cop 60LWT -1 ambient. | 5 | EUROVENT | EN14825 EN14511 | ISO 9614 | Electa Maxi
|  |  | Small Commercial/Residential Space Heating, Cooling,DHW | Air Sourced / Inverter Scroll | Propane R290 | 20.8-34.9 | 80° C | 1 year standard - up to 5 years at additional cost | #VALUE! | 3.07 cop 60LWT 16.5 ambient | 2.16 cop 60LWT -1 Ambient | -20 | EUROVENT,CE | EN14825 EN14511 | ISO 9614 | MidiPACK-PI
|  |  | Large Commercial/Residential Space Heating, Cooling | Air Sourced / Inverter Scroll | Propane R290 | 38.2-64.7 | 80° C | 1 year standard - up to 5 years at additional cost | #VALUE! |  |  | -20 | EUROVENT,CE | EN14825 EN14511 | ISO 9614 | MidiPACK-PI
|  |  | Large Commercial/Residential Space Heating, Cooling | Air Sourced / Inverter Scroll | Propane R290 | 72.1-159.2 | 78° C | 1 year standard - up to 5 years at additional cost | #VALUE! | 3.02 cop 60LWT 16.5 Ambient | 2.1 cop 60LWT -1 Ambient | -20 | EUROVENT | EN14825 EN14511 | ISO 9614 | UniPACK-PI
|  |  | Large Commercial/Residential Space Heating, Cooling | Air Sourced / Inverter Scroll | HFC R32 | 70.3-127.3 | 60° C | 1 year standard - up to 5 years at additional cost | #VALUE! | 2.84 cop 60LWT 16.5 Ambient |  | 5 | EUROVENT | EN14825 EN14511 | ISO 9614 | Easy Pack I ECO
|  |  | Large Commercial/Residential Space Heating, Cooling | Air Sourced / Inverter Scroll | Propane R290 | 50.1-163.7 | 72° C | 1 year standard - up to 5 years at additional cost | #VALUE! |  |  | -20 | EUROVENT,CE | EN14825 EN14511 | ISO 9614 | UniPACK-P
|  |  | Large Commercial/Industrial Space Heating, Cooling | Air Sourced/ Scroll Compressor | HFC R454B | 77.8-197.4 | 65° C | 1 year standard - up to 5 years at additional cost | #VALUE! |  | 2.24 cop 60LWT -1 Ambient | -15 | EUROVENT | EN14825 EN14511 | ISO 9614 | EasyPACK & WinPACK EC HT
|  |  | Large Commercial/Industrial Space Heating, Cooling | Air Sourced/ Scroll Compressor | HFC R454B | 368.3-1308.8 | 57° C | 1 year standard - up to 5 years at additional cost | #VALUE! |  |  | -15 | EUROVENT | EN14825 EN14511 | ISO 9614 | WinPOWER ECO / TWIN
MAXA |  |  | Small Commercial/Residential Space HEATING, DHW | Air Sourced/ Inverter Rotary | Propane R290 | 6-50 | 60° C | 3 year standard - up to 5 yeats at additional cost | #VALUE! |  |  |  | EUROVENT |  |  | i290
|  |  | Small Commercial/Residential Space HEATING, DHW | Air Sourced/ Inverter Twin Rotary | HFC R32 | 6.16-18 | 58° C | 3 year standard - up to 5 yeats at additional cost | #VALUE! |  |  |  | EUROVENT |  |  | i-32V5
|  |  | Small Commercial/Residential Space HEATING, DHW | Air Sourced/ Rotary | HFC R32 | 21-32 | 58° C | 3 year standard - up to 5 yeats at additional cost | #VALUE! |  |  |  | EUROVENT |  |  | i-32V5H-MIDI
|  |  | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Scroll | HFC R32 | 40.6-66.6 | 40° C | 3 year standard - up to 5 yeats at additional cost | #VALUE! |  |  |  | EUROVENT |  |  | i-HPV5H
|  |  | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Scroll | HFC R410a | 65.8-82.1 | 65° C | 3 year standard - up to 5 yeats at additional cost | #VALUE! |  |  |  | EUROVENT |  |  | I-MAX
EMERALD |  |  | Small Commercial/Residential DHW | AirSourced/ Inverter Scroll | Propane R290 | 2.8kw | 60°/70° C | Select -5 Years tank & system, 2 years service, Pro - 7 years tank, 5 years labour & service | #VALUE! | Select 4.41 cop at 20 ambient, Pro 4.8-5.2 cop 20 Ambient, No Element, 15-55c |  |  | AS/NZS 4234 |  |  | All-In-One Pro, Hitachi JV compressor
CLIVET | MASTERFLOW (Updated 9-10-2026) | Jethro.brown@masterflow.net.au | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Rotary &Scroll, Reversible | Propane R290 | 35-85kW | 75° C | 1 year standard- up to 5 as an option | Maintained as per the Masterflow IOM |  |  |  | EUROVENT | EN14511 AHRI 551 / 594 | ISO 9614 | Thunder, WiSAN-P, modular
|  |  | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Scroll, Reversible | HFC R32 | 110-252Kw | 60c | 1 year standard- up to 5 as an option | Maintained as per the Masterflow IOM |  |  |  | EUROVENT | EN14511 AHRI 551 / 594 | ISO 9614 | WiSAT-YEE1
|  |  | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Scroll, | HFC R32 | 52-128kw | 60c | 1 year stanard - up to 5 as an option | Maintained as per the Masterflow IOM |  |  |  | EUROVENT | EN14511 AHRI 551 / 594 | ISO 9614 | Sheen EVO
|  |  | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Scroll, | HFC R32 | 710-1211Kw | 55c | 1 year stanard - up to 5 as an option | Maintained as per the Masterflow IOM |  |  |  | EUROVENT | EN14511 AHRI 551 / 594 | ISO 9614 | SPINchiller4 WSAN-YSC4
|  |  | Large Commercial/Residential Space Heating, Cooling,DHW | AirSourced/ Inverter Scroll, | HFC R32 | 50-91kw | 55C | 1 year stanard - up to 5 as an option | Maintained as per the Masterflow IOM |  |  |  | EUROVENT | EN14511 AHRI 551 / 594 | ISO 9614 | ELFOEnergy Storm EVO WSAT-YES
DAIKIN | DAIKIN AUSTRALIA |  | Large Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll | HFC R32 HFC R410a | 80 - 630 20 - 600 | 60° C | [5 empty] | EUROVENT/AHRI | EN14825 EN14511 ASHRAE 90.1 AHRI 551/593 | ISO 9614
|  |  | Large Commercial/Residential Space Heating | Air-Sourced / Scroll | HFC R134a | 250 - 600 | 55° C
MITSUBISHI (CLIMAVENETA) | MITSUBISHI AUSTRALIA |  | Small Commercial/Residential DHW | Air-Sourced / Scroll | CO2 R744 | 5-40 | 90° C | [5 empty] | EUROVENT/AHRI | EN14825 EN14511 ASHRAE 90.1 AHRI 551/594 | ISO 9614
|  |  | Small Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll | HFC R407C | 5-45 | 70° C
|  |  | Small Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll | HFC R32 | 50 - 110 | 65° C
|  |  | Large Commercial/Industrial Space Heating | Water-Sourced / Screw | HFO R1234ze HFC R134a | 300 - 1400 | 50° C
BLUEBOX | EUROTHERMAL |  | Large Commercial/Residential Space Heating, DHW | Air-Sourced / Scroll | HFC R454B HFC R410a | 40 - 900 | 65° C | [5 empty] | EUROVENT | EN14825 EN14511 | ISO 9614
|  |  | Large Commercial/Residential Space Heating | Air-Sourced / Screw | HFO R1234ze HFC R134a | 300 - 1900 | 55° C
|  |  | Large Commercial/Residential Space Heating | Water-Sourced / Screw | HFO R1234ze HFC R134a | 200 - 1100 | 50° C
Note on K9: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: email from GN to JK, dated 1.10.26